Report date: 31st August 2010

Table: Average water quality for Kampala during the period of 23rd  - 29th August 10

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.2 | 7.2 | 6.8 | 7.0 | 7.1 | 6.9 | 6.7 | 6.5- 8.5 |
| Turbidity | NTU | 25.5 | 0.16 | 0.25 | 0.17 | 0.12 | 0.12 | 0.66 | 5.00 |
| Colour | PTU | 172 | 2 | 1 | 3 | 3 | 1 | 4 | 15 |
| Free chlorine | mg/l | NA | 1.20 | 0.30 | 0.25 | 0.25 | 0.30 | 0.25 | 0.2-0.5 |
| E-Coli | CFU/100 ml | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable