Report date: 21sth March 2011

Table: Average water quality for Kampala during the period of 14th - 20th March 11

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.6 | 7.3 | 7.2 | 7.1 | 7.1 | 7.0 | 7.3 | 6.5- 8.5 |
| Turbidity | NTU | 19.8 | 0.88 | 0.69 | 0.62 | 0.97 | 0.68 | 0.49 | 5.00 |
| Colour | PTU | 201 | 7 | 9 | 7 | 8 | 4 | 6 | 15 |
| Free chlorine | mg/l | NA | 1.30 | 0.40 | 0.30 | 0.35 | 0.30 | 0.35 | 0.2-0.5 |
| E-Coli | CFU/100 ml | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable