Report date: 24th January 2011

Table: Average water quality for Kampala during the period of 17th - 23rd January 11

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.7 | 7.3 | 7.1 | 7.2 | 7.0 | 7.0 | 7.1 | 6.5- 8.5 |
| Turbidity | NTU | 12 | 0.86 | 0.58 | 0.28 | 0.45 | 0.39 | 0.42 | 5.00 |
| Colour | PTU | 175 | 0 | 1 | 2 | 2 | 0 | 3 | 15 |
| Free chlorine | mg/l | NA | 1.10 | 0.30 | 0.30 | 0.25 | 0.30 | 0.30 | 0.2-0.5 |
| E-Coli | CFU/100 ml | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable