Report date: 9th August 2010

Table: Average water quality for Kampala during the period of 2nd  - 8th August 10

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.7 | 7.3 | 7.1 | 7.2 | 7.1 | 6.9 | 7.1 | 6.5- 8.5 |
| Turbidity | NTU | 22.5 | 0.40 | 0.25 | 0.40 | 0.30 | 0.19 | 0.35 |  5.00 |
| Colour | PTU | 142 | 6 | 4 | 3 | 5 | 3 | 5 |  15 |
| Free chlorine | mg/l | NA | 1.20 | 0.35 | 0.40 | 0.35 | 0.35 | 0.35 | 0.2-0.5 |
| E-Coli | CFU/100 ml | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable