Report date: 07th September 2010

Table: Average water quality for Kampala during the period of 30th August- 05th September 10

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.1 | 6.8 | 6.7 | 6.7 | 6.6 | 6.7 | 6.6 | 6.5- 8.5 |
| Turbidity | NTU | 28 | 0.15 | 0.22 | 0.18 | 0.14 | 0.16 | 0.66 | 5.00 |
| Colour | PTU | 112 | 2 | 4 | 3 | 3 | 1 | 5 | 15 |
| Free chlorine | mg/l | NA | 1.10 | 0.35 | 0.30 | 0.30 | 0.30 | 0.25 | 0.2-0.5 |
| E-Coli | CFU/100 ml | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable