Report date: 5th July 2010

Table: Average water quality for Kampala during the period of 28th June - 4th July 10

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.5 | 7.3 | 6.9 | 7.0 | 7.2 | 6.9 | 7.1 | 6.5- 8.5 |
| Turbidity | NTU | 14.5 | 0.50 | 0.21 | 0.18 | 0.22 | 0.16 | 0.19 |  5.00 |
| Colour | PTU | 140 | 0 | 1 | 3 | 4 | 0 | 3 |  15 |
| Free chlorine | mg/l | NA | 1.10 | 0.45 | 0.40 | 0.40 | 0.45 | 0.35 | 0.2-0.5mg/l |
| E-Coli | CFU/100 ml | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable