Report date: 26th April 2010

Table: Average water quality for Kampala during the period of 19th - 25th April 10

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.30 | 7.05 | 6.95 | 6.99 | 7.08 | 7.22 | 7.03 | 6.5- 8.5 |
| Turbidity | NTU | 15.3 | 0.80 | 0.19 | 0.25 | 0.35 | 0.16 | 0.48 |  5.00 |
| Colour | PTU | 186 | 0 | 2 | 1 | 13 | 4 | 7 |  15 |
| Free chlorine | mg/l | - | 0.90 | 0.35 | 0.30 | 0.50 | 0.30 | 0.30 | 0.20 |
| E-Coli | CFU/100 ml | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Strepstococi | CFU/ 100 ml | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable