Report date: 28th June 2010

Table: Average water quality for Kampala during the period of 21st - 27th June 10

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.3 | 7.2 | 6.9 | 7.0 | 7.0 | 6.9 | 6.8 | 6.5- 8.5 |
| Turbidity | NTU | 11.2 | 0.72 | 0.28 | 0.19 | 0.21 | 0.18 | 0.38 |  5.00 |
| Colour | PTU | 128 | 5 | 1 | 0 | 5 | 0 | 4 |  15 |
| Free chlorine | mg/l | - | 1.25 | 0.25 | 0.35 | 0.30 | 0.35 | 0.30 | 0.20 |
| E-Coli | CFU/100 ml | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable