Report date: 22nd July 2013

Table: Average water quality for Kampala during the period of 15th– 21st July 2013

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality (Water in Supply) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.2 | 7.0 | 6.8 | 6.9 | 6.9 | 7.0 | 7.0 | 6.5 – 8.5 |
| Turbidity | NTU | 9.8 | 0.78 | 0.56 | 0.50 | 0.65 | 0.38 | 0.68 | ≤5 |
| Colour | PTU | 80 | 2 | 2 | 3 | 5 | 0 | 5 | ≤15 |
| Free chlorine | mg/l | NA | 1.40 | 0.30 | 0.35 | 0.30 | 0.35 | 0.35 | 0.20 – 0.50 |
| E-Coli | CFU/100 ml | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Coliforms | CFU/ 100 ml | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable