Report date: 22nd February 2010

Table: Average water quality for Kampala during the period of 15th - 21st February 10

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.60 | 7.29 | 7.13 | 7.10 | 7.02 | 7.08 | 7.15 | 6.5- 8.5 |
| Turbidity | NTU | 18.5 | 0.80 | 0.44 | 0.38 | 0.24 | 0.32 | 0.52 |  5.00 |
| Colour | PTU | 168 | 4 | 6 | 3 | 1 | 1 | 8 |  15 |
| Free chlorine | mg/l | - | 1.10 | 0.35 | 0.25 | 0.35 | 0.30 | 0.35 | 0.20 |
| E-Coli | CFU/100 ml | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Strepstococi | CFU/ 100 ml | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable