Report date: 25th January 2010

Table: Average water quality for Kampala during the period of 18th - 24th January 10

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.80 | 7.11 | 7.08 | 7.03 | 7.09 | 7.01 | 7.06 | 6.5- 8.5 |
| Turbidity | NTU | 14.5 | 1 | 0.75 | 0.58 | 0.75 | 0.52 | 0.85 |  5.00 |
| Colour | PTU | 132 | 2 | 5 | 4 | 3 | 2 | 7 |  15 |
| Free chlorine | mg/l | - | 1.40 | 0.30 | 0.30 | 0.35 | 0.35 | 0.35 | 0.20 |
| E-Coli | CFU/100 ml | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Strepstococi | CFU/ 100 ml | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable