Report date: 28th September 2009

Table: Average water quality for Kampala during the period of 21st- 27th September 2009

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.60 | 7.70 | 7.16 | 7.08 | 7.16 | 7.20 | 7.15 | 6.5- 8.5 |
| Turbidity | NTU | 18 | 1.20 | 0.58 | 0.47 | 1.30 | 0.38 | 0.85 |  5.00 |
| Colour | PTU | 148 | 1 | 4 | 3 | 13 | 6 | 14 |  15 |
| Free chlorine | mg/l | - | 1.20 | 0.30 | 0.30 | 0.40 | 0.30 | 0.35 | 0.20 |
| E-Coli | CFU/100 ml | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Strepstococi | CFU/ 100 ml | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable