Report date: 02nd March 2015

Table: Average water quality for Kampala during the period of 23rd Feb – 01st March 2015

| Parameter | Monitoring points |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.2 | 7.0 | 7.1 | 7.1 | 7.0 | 7.1 | 6.5- 8.5 |
| Turbidity | NTU | 0.35 | 0.41 | 0.39 | 0.43 | 0.21 | 0.47 | ≤ 5.00 |
| Colour | PTU | 2 | 3 | 2 | 4 | 2 | 4 | ≤ 15 |
| Free chlorine | mg/l | 0.50 | 0.35 | 0.30 | 0.30 | 0.25 | 0.28 | 0.2-0.5 |
| E-Coli | CFU/100 ml | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 0 | 0 | 0 | 0 | 0 | 0 | 0 |