Report date: 31 st August 2009

Table: Average water quality for Kampala during the period of 24 th – 30th August 2009

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 8.20 | 7.20 | 7.10 | 7.08 | 7.01 | 7.13 | 7.22 | 6.5- 8.5 |
| Turbidity | NTU | 95.20 | 1.10 | 0.64 | 0.48 | 0.81 | 0.28 | 0.67 |  5.00 |
| Colour | PTU | 451 | 2 | 8 | 4 | 9 | 0 | 8 |  15 |
| Free chlorine | mg/l | - | 1.10 | 0.40 | 0.30 | 0.35 | 0.30 | 0.30 | 0.20 |
| E-Coli | CFU/100 ml | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Strepstococi | CFU/ 100 ml | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable