Report date: 3rd June 2013

Table: Average water quality for Kampala during the period of 27th May – 2nd June 2013

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality (Water in Supply) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 7.1 | 6.9 | 6.9 | 6.9 | 7.0 | 7.0 | 7.0 | 6.5 – 8.5 |
| Turbidity | NTU | 11.0 | 0.57 | 0.54 | 0.59 | 0.61 | 0.70 | 0.68 | ≤5 |
| Colour | PTU | 121 | 2 | 2 | 2 | 2 | 0 | 4 | ≤15 |
| Free chlorine | mg/l | NA | 1.20 | 0.35 | 0.30 | 0.25 | 0.30 | 0.25 | 0.20 – 0.50 |
| E-Coli | CFU/100 ml | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable