Report date: 11th February 2013

Table: Average water quality for Kampala during the period of 4th - 10th Feb. 2013

| Parameter | Monitoring points |  |  |  |  |  |  |  | National Standard For potable water quality (Water in Supply) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unit | Raw water | Treated Water Water Works | Water in Supply |  |  |  |  |  |
|  |  |  |  | Rubaga Division | Nakawa Division | Makindye Division | Kampala Central | Kawempe Division |  |
| pH | … | 8.3 | 7.2 | 7.1 | 7.1 | 7.0 | 7.0 | 7.1 | 6.5 – 8.5 |
| Turbidity | NTU | 19.9 | 0.72 | 0.68 | 0.59 | 0.61 | 0.70 | 0.68 | ≤5 |
| Colour | PTU | 170 | 3 | 4 | 3 | 5 | 1 | 6 | ≤15 |
| Free chlorine | mg/l | NA | 1.10 | 0.40 | 0.30 | 0.25 | 0.30 | 0.30 | 0.20 – 0.50 |
| E-Coli | CFU/100 ml | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Faecal -Streptococi | CFU/ 100 ml | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

NA: Not applicable